

*NIU Design and Construction Standards*

*Division 26 2923 – Variable Frequencty Controllers*

September 2012, rev 00

**26 2923 – Variable Frequency Controllers**

PART 1.

1.01

GENERAL

Description

A.

This specification is to cover a complete Variable Frequency motor Drive (VFD) consisting of a pulse width modulated (PWM) inverter designed for use on a standard NEMA Design B induction motor.

B.

The drive manufacturer shall supply the drive and all necessary options as herein specified. VFD’s that are manufactured by a third party and “brand labeled” shall not be acceptable. All VFDs installed on individual projects shall be from the same manufacturer.

C.

New or replacement products installed in existing facilities shall be consistent with existing equipment.

D.

Products shall be provided by:

1.

2.

3.

Toshiba ([www.toshiba.com)](http://www.toshiba.com/) ABB [(www.abb.us/drives)](http://www.abb.us/drives)) Allen Bradley [(www.ab.com)](http://www.ab.com/)

1.02

Quality Assurance

A. Referenced Standards:

1.

2.

3.

4.

5.

6.

Standard 519-1992, IEEE Guide for Harmonic Content and Control. UL508C

ICS 7.0, AC Adjustable Speed Drives IEC 16800 Parts 1, 2 and 3

NEC 430.120, Adjustable-Speed Drive Systems

IBC 2006 Seismic – referencing ASC 7-05 and ICC AC-156

B. Qualifications:

1. VFDs and options shall be UL listed as a complete assembly. The base VFD shall be UL listed for 100 KAIC without the need for input fuses.
2. CE Mark – The VFD shall meet product standard EN 61800-3 for the First Environment restricted level. (RFI / EMI Filter spec).

1.03

Submittals

A. Submittals shall include the following information:

Variable Frequency Controllers Div 22 1316 Page 1 of 5



*NIU Design and Construction Standards*

*Division 26 2923 – Variable Frequencty Controllers*

1.

2.

3.

4.

Outline dimensions, conduit entry locations and weight. Customer connection and power wiring diagrams.

Complete technical product description including a complete list of options. Compliance to IEEE 519 – harmonic analysis for particular jobsite including total harmonic voltage distortion and total harmonic current distortion (TDD).

a).

All VFD’s shall include a minimum of 3% impedance reactors, no exceptions.

PART 2.

PRODUCTS

2.01

Variable Frequency Drives

A.

The VFD package as specified herein shall be enclosed in a UL Listed Type enclosure, (enclosures with only NEMA ratings are not acceptable.

1. Environmental operating conditions: 0 to 400 C (32 to 1040 F) continuous. Altitude 0 to 3300 feet above sea level, less than 95% humidity, non- condensing. All circuit boards shall have conformal coating.
2. Enclosure shall be UL rated and shall be UL listed as a plenum rated VFD.

B.

All VFDs shall have the following standard features:

1.

All VFDs shall have the same customer interface, including digital display, and keypad, regardless of horsepower rating. The keypad shall be removable, capable of remote mounting and allow for uploading and downloading of parameter settings as an aid for start-up of multiple VFDs.

The keypad shall include Hand-Off-Auto selections or equivalent and manual speed control. There shall be fault reset on the keypad.

The VFD shall have internal 3% impedance reactors to reduce the harmonics to the power line and to add protection from AC line transients.

The input current rating of the VFD shall be no more than 3% greater than the output current rating. VFD’s with higher input current ratings require the upstream wiring, protection devices, and source transformers to be oversized per NEC 430.120.

The VFD shall provide a programmable loss-of-load (broken belt / broken coupling) Form-C relay output. The drive shall be programmable to signal the loss-of-load condition via a keypad warning, Form-C relay output, and / or over the serial communications bus.

2.

3.

4.

5.

C.

All VFDs to have the following adjustments:

1. Run permissive circuit - There shall be a run permissive circuit for damper or valve control. Regardless of the source of a run command (keypad command, input contact closure, time-clock control, or serial communications), the VFD shall provide a dry contact closure that will signal the damper to open (VFD

Variable Frequency Controllers Div 22 1316 Page 2 of 5



*NIU Design and Construction Standards*

*Division 26 2923 – Variable Frequencty Controllers*

motor does not operate). When the damper is fully open, a normally open dry contact (end-switch) shall close. The closed end-switch is wired to a VFD digital input and allows VFD motor operation. A minimum of two separate safety interlock inputs shall be provided. When any safety is opened, the motor shall be commanded to coast to stop and the damper shall be commanded to close.

The VFD control shall include a programmable time delay for VFD start and a keypad indication that this time delay is active. A Form C relay output provides a contact closure to signal the VAV boxes open. This will allow VAV boxes to be driven open before the motor operates.

The VFD shall include a fireman’s override input. The mode shall override all other inputs (analog/digital, serial communication, and all keypad commands), except customer defined safety run interlocks, and force the motor to run at a preset speed or in a separate PID mode.

2.

3.

D.

EMI / RFI filters: All VFD’s shall include EMI/RFI filters. The onboard filters shall allow the entire VFD assembly to be CE Marked and the VFD shall meet product standard EN 61800-3 for the First Environment restricted. No Exceptions.

E.

Bypass Controller

1.

A complete factory wired and tested bypass system consisting of a door interlocked, pad lockable circuit breaker, output contactor, bypass contactor, and fast acting VFD isolation fuses.

2.

The bypass enclosure door and VFD enclosure must be mechanically interlocked such that the disconnecting device must be in the “Off” position before either enclosure may be accessed.

3.

The VFD and bypass package shall have a UL listed short circuit current rating (SCCR) of 100,000 amps and this rating shall be indicated on the UL data label.

4.

Drive Isolation Fuses - To ensure maximum possible bypass operation, fast acting fuses, exclusive to the VFD, shall be provided to allow the VFD to disconnect from the line prior to clearing upstream branch circuit protection. This maintains bypass operation capability in the event of a VFD failure.

Bypass designs, which have no such fuses will not be accepted.

5.

The system (VFD and Bypass) tolerated voltage window shall allow the system to operate from a line of +30%, -35% nominal voltage range. The system shall incorporate circuitry that will allow the drive or bypass contactor to remain “sealed in” over this voltage tolerance at a minimum.

6.

The bypass shall maintain positive contactor control throughout the voltage tolerance window of nominal voltage ± 10 %.

Variable Frequency Controllers Div 22 1316 Page 3 of 5



*NIU Design and Construction Standards*

*Division 26 2923 – Variable Frequencty Controllers*

7.

Motor protection from single phase power conditions - the bypass system must be able to detect a single phase input power condition while running in bypass, disengage the motor in a controlled fashion, and give a single phase input power indication. Bypass systems not incorporating single phase protection in bypass mode are not acceptable.

8.

The bypass system shall NOT depend on the VFD for bypass operation. The bypass system shall be designed for stand-alone operation and shall be completely functional in both Hand and Automatic modes even if the VFD has been removed from the system for repair / replacement.

9.

The bypass control shall include a programmable time delay for bypass start and keypad indication that this time delay is in process. A Form C relay output provides a contact closure to signal the VAV boxes open. This will allow VAV boxes to be driven open before the motor operates at full speed in the bypass mode. The time delay shall be field programmable from 0 – 120 seconds.

PART 3.

EXECUTION

3.01

Installation

A.

Installation shall be the responsibility of the contractor.

B.

Power wiring shall be completed by the contractor, to NEC code 430.122 wiring requirements based on the VFD input current.

C.

The contractor shall complete all wiring in accordance with the recommendations of the VFD manufacturer as outlined in the VFD installation manual.

3.02

Start-up

A. Certified factory start-up shall be provided for each drive by a factory authorized service center.

3.03

Warranty

A. The VFD Product Warranty shall be 24 months from the date of certified start-up, not to exceed 30 months from the date of shipment. The warranty shall include all parts, labor, travel time and expenses. A toll free 24/365 technical support line shall be available.

Variable Frequency Controllers Div 22 1316 Page 4 of 5



*NIU Design and Construction Standards*

*Division 26 2923 – Variable Frequencty Controllers*

End of Division 26 2923

**This section of the NIU Design and Construction Standards establishes minimum**

**requirements only.**

**It should not be used as a complete specification.**

Variable Frequency Controllers Div 22 1316

Page 5 of 5